## Cover Page
Annual Legionella Monitoring Records
| Year | 2025
| LM Number: | LM2033
| Company Name: | Test Company
| Company Address: | 52 North Lane, Aldershot, Hampshire. GU12 4UB
| Contact Name: | Daniel Danon
| Contact Email: | daniel@legionelladossier.com
| Contact Number: | 2444666668888888

## Monthly Outlet
|  | (Where a TMV is intalled, record the feed temperature) |  |  | Monlthy Temperature Monitoring Records
Date | Outlet/Location | Cold Mains Water Temperature °C | Cold Tank Water Temperature °C | Hot Water Temperature °C | Name | Comments
Unit 3
2025-02-05 | 1st Floor- Finance Office | 11 | - | 51 | Tim Lees
2025-02-05 | 1st Floor- Office Female Toilets | 11 | - | 51 | Tim Lees
2025-02-05 | Factory/ Male Toilets | 11 | - | 51 | Tim Lees
2025-02-05 | Workshop Kitchen Area | 14 | - | 60 | Tim Lees
2025-02-05 | Directors Office Sink | 10 | - | 52 | Tim Lees
2025-02-05 | Deburring Workshop | 10 | - | 50 | Tim Lees
2025-02-05 | Cleaning Room- Bib Tap | 11 | - | - | Tim Lees
2025-02-05 | Outside- Bib Tap | 9 | - | - | Tim Lees
2025-02-05 | GF Visitors WC | 11 | - | 50 | Tim Lees
2025-02-05 | Rumbler Bib Tap (hot) | - | - | 52 | Tim Lees
Unit 11
2025-02-05 | Mezzanine Kitchenette | 10 | - | 52 | Tim Lees
2025-02-05 | Mezzanine Male Toilets | 12 | - | 58 | Tim Lees
2025-02-05 | Mezzanine Female Toilets | 12 | - | 58 | Tim Lees
2025-02-05 | Workshop- Next Roller Shutter Doors | 16 | - | - | Tim Lees
2025-02-05 | Workshop- Near Fire Exit Door | 18 | - | - | Tim Lees
Unit 14/15
2025-02-05 | Workshop Toilets - Wash Hand Basin unit 14 | 10 | - | 59 | Tim Lees
2025-02-05 | Outside Bib Tap | 10 | - | - | Tim Lees
2025-02-05 | Workshop Toilets - Wash Hand Basin unit 15 | 11 | - | 58 | Tim Lees
2025-02-05 | Workshop Sink unit 14 | 10 | - | 59 | Tim Lees
2025-02-05 | Mezzanine unit 14 | 11 | - | 58 | Tim Lees
Unit 16
2025-02-05 | Workshop Toilets - Wash Hand Basin | 11 | - | 42 | Tim Lees | TMV (Hot): 56
2025-02-05 | Workshop Toilets - Bib Tap | 12 | - | - | Tim Lees
2025-02-05 | Mezzanine- Sink | 12 | - | 52 | Tim Lees
Unit 19
2025-02-05 | Workshop Toilets | - | - | - | Tim Lees | No Access- Unit being emptied
2025-02-05 | Workshop Restroom | - | - | - | Tim Lees | No Access- Unit being emptied
2025-02-05 | Workshop - Bib Tap | - | - | - | Tim Lees | No Access- Unit being emptied
Unit 10- The Christy Estate
2025-02-05 | Entrances Male Toilets | 12 | - | 55 | Tim Lees | what 3 words: brief.eagle.sums
2025-02-05 | Entrances Female Toilets | 12 | - | 48 | Tim Lees
2025-02-05 | Kitchenette | 12 | - | 55 | Tim Lees
2025-02-05 | Workshop - Next to Tank | 17 | - | - | Tim Lees
2025-02-05 | Workshop - Next to Boiler | 12 | - | - | Tim Lees
2025-02-05 | Workshop - Fire Exit Doors | 16 | - | - | Tim Lees
2025-02-05 | Outside | 14 | - | - | Tim Lees
Unit 1
2025-02-05 | Male Toilets | 13 | - | 42 | Tim Lees | TMV (Hot): 54
2025-02-05 | Female Toilets | 13 | - | 52 | Tim Lees
2025-02-05 | Kitchenette mezzanine floor | 14 | - | 57 | Tim Lees
2025-02-05 | Workshop - Next To Toilets bib tap | 13 | - | - | Tim Lees
2025-02-05 | Workshop - Next To Fire Exit Doors bib tap | 14 | - | - | Tim Lees
Unit 3
2025-02-27 | GF Visitors WC | 11 | - | 54 | Tim Lees
2025-02-27 | Rumbler Bib Tap (hot) | - | - | 52 | Tim Lees
2025-02-27 | 1st Floor- Finance Office | 11 | - | 54 | Tim Lees
2025-02-27 | 1st Floor- Office Female Toilets | 11 | - | 51 | Tim Lees
2025-02-27 | Factory/ Male Toilets | 13 | - | 52 | Tim Lees
2025-02-27 | Workshop Kitchen Area | 13 | - | 59 | Tim Lees
2025-02-27 | Directors Office Sink | 10 | - | 50 | Tim Lees
2025-02-27 | 1st floor- Deburring Workshop | 12 | - | 54 | Tim Lees
2025-02-27 | 1st floor- Cleaning Room- Bib Tap | 14 | - | - | Tim Lees
2025-02-27 | Outside- Bib Tap | 11 | - | - | Tim Lees
Unit 11
2025-02-27 | Mezzanine Kitchenette | 10 | - | 53 | Tim Lees
2025-02-27 | Mezzanine Male Toilets | 11 | - | 51 | Tim Lees
2025-02-27 | Mezzanine Female Toilets | 11 | - | 51 | Tim Lees
2025-02-27 | Workshop- Next Roller Shutter Doors | 15 | - | - | Tim Lees
2025-02-27 | Workshop- Near Fire Exit Door | 18 | - | - | Tim Lees
Unit 14/15
2025-02-27 | Unit 15- Workshop Toilets WHB | 11 | - | 56 | Tim Lees
2025-02-27 | Unit 14 - Workshop Toilets WHB | 11 | - | 62 | Tim Lees
2025-02-27 | Unit 14- Workshop Sink | 11 | - | 62 | Tim Lees
2025-02-27 | Unit 14- Mezzanine Sink | 11 | - | 59 | Tim Lees
2025-02-27 | Unit 14 - Outside Bib Tap | 12 | - | - | Tim Lees
Unit 16
2025-02-27 | Workshop Toilets - WHB | 11 | - | 42 | Tim Lees | TMV (Hot): 58
2025-02-27 | Workshop Bib Tap (near toilet) | 11 | - | - | Tim Lees
2025-02-27 | Mezzanine- Sink | 12 | - | 50 | Tim Lees
Unit 19
2025-02-27 | Workshop Toilets | 12 | - | 39 | Tim Lees | TMV (Hot): 50
2025-02-27 | Workshop Restroom/ Kitchen | 12 | - | 50 | Tim Lees
2025-02-27 | Workshop - Bib Tap | 14 | - | - | Tim Lees
Unit 1
2025-02-27 | Male Toilets | 12 | - | 42 | Tim Lees | TMV (Hot): 52
2025-02-27 | Female Toilets | 13 | - | 52 | Tim Lees
2025-02-27 | Kitchenette mezzanine floor | 14 | - | 52 | Tim Lees
2025-02-27 | Workshop - Next To Toilets bib tap | 12 | - | - | Tim Lees
2025-02-27 | Workshop - Next To Fire Exit Doors bib tap | 16 | - | - | Tim Lees
Unit 10- The Christy Estate
2025-02-27 | Entrances Male Toilets | 11 | - | 54 | Tim Lees | what 3 words: brief.eagle.sums
2025-02-27 | Entrances Female Toilets | 12 | - | 56 | Tim Lees
2025-02-27 | Kitchenette | 12 | - | 53 | Tim Lees
2025-02-27 | Workshop - Next to Tank | 16 | - | - | Tim Lees
2025-02-27 | Workshop - Next to Boiler | 15 | - | - | Tim Lees
2025-02-27 | Workshop - Fire Exit Doors | 18 | - | - | Tim Lees
2025-02-27 | Outside | 14 | - | - | Tim Lees
Unit 2- New Office
2025-02-27 | Factory Floor- Bib Tap | 18 | - | - | Tim Lees
2025-02-27 | Ground Floor- Factory Kitchen | 11 | - | 52 | Tim Lees
2025-02-27 | Ground Floor- Male Toile off Factory Kitchen | 11 | - | 42 | Tim Lees | TMV (Hot):
2025-02-27 | Ground Floor- Factory Male Toilets | 10 | - | 52 | Tim Lees
2025-02-27 | Ground Floor- Factory Male Toilets cubicle | 10 | - | 40 | Tim Lees | TMV (Hot):
2025-02-27 | Ground Floor Visitors Toilet | 11 | - | 44 | Tim Lees | TMV (Hot):
2025-02-27 | 1st Floor- Female Toilets | 10 | - | 47 | Tim Lees
2025-02-27 | 1st Floor- Male Toilets | 10 | - | 42 | Tim Lees
2025-02-27 | 1st Floor- Office Kitchen | 12 | - | 45 | Tim Lees
Unit 3
2025-03-25 | GF Visitors WC | 13 | - | 54 | Tim Lees, Elliot Turner
2025-03-25 | Rumbler Bib Tap (hot) | - | - | 52 | Tim Lees, Elliot Turner
2025-03-25 | 1st Floor- Finance Office | 12 | - | 54 | Tim Lees, Elliot Turner
2025-03-25 | 1st Floor- Office Female Toilets | 12 | - | 53 | Tim Lees, Elliot Turner
2025-03-25 | Factory/ Male Toilets | 13 | - | 13 | Tim Lees, Elliot Turner | No hot water
2025-03-25 | Workshop Kitchen Area | 14 | - | 53 | Tim Lees, Elliot Turner
2025-03-25 | Directors Office Sink | 13 | - | 55 | Tim Lees, Elliot Turner
2025-03-25 | 1st floor- Deburring Workshop | 15 | - | 54 | Tim Lees, Elliot Turner
2025-03-25 | 1st floor- Cleaning Room- Bib Tap | 17 | - | - | Tim Lees, Elliot Turner
2025-03-25 | Outside- Bib Tap | 16 | - | -
Unit 11
2025-03-25 | Mezzanine Kitchenette | 13 | - | 56 | Tim Lees, Elliot Turner
2025-03-25 | Mezzanine Male Toilets | 13 | - | 56 | Tim Lees, Elliot Turner
2025-03-25 | Mezzanine Female Toilets | 11 | - | 51 | Tim Lees, Elliot Turner
2025-03-25 | Workshop- Next Roller Shutter Doors | 17 | - | - | Tim Lees, Elliot Turner
2025-03-25 | Workshop- Near Fire Exit Door | 17 | - | - | Tim Lees, Elliot Turner
Unit 14/15
2025-03-25 | Unit 15- Workshop Toilets WHB | 12 | - | 59 | Tim Lees, Elliot Turner
2025-03-25 | Unit 14 - Workshop Toilets WHB | 14 | - | 62 | Tim Lees, Elliot Turner
2025-03-25 | Unit 14- Workshop Sink | 14 | - | 62 | Tim Lees, Elliot Turner
2025-03-25 | Unit 14- Mezzanine Sink | 13 | - | 56 | Tim Lees, Elliot Turner
2025-03-25 | Unit 14 - Outside Bib Tap | 12 | - | - | Tim Lees, Elliot Turner
Unit 16
2025-03-25 | Workshop Toilets - WHB | 13 | - | 42 | Tim Lees, Elliot Turner | TMV (Hot) PRE - 54
2025-03-25 | Workshop Bib Tap (near toilet) | 17 | - | - | Tim Lees, Elliot Turner
2025-03-25 | Mezzanine- Sink | 12 | - | 50 | Tim Lees, Elliot Turner
Unit 19
2025-03-25 | Workshop Toilets | 13 | - | 41 | Tim Lees | No access
2025-03-25 | Workshop Restroom/ Kitchen | 12 | - | 50 | Tim Lees | No access
2025-03-25 | Workshop - Bib Tap | 16 | - | - | Tim Lees | No access
Unit 1
2025-03-25 | Male Toilets | 13 | - | 41 | Tim Lees, Elliot Turner | TMV (Hot)PRE : 54
2025-03-25 | Female Toilets | 13 | - | 42 | Tim Lees, Elliot Turner
2025-03-25 | Kitchenette mezzanine floor | 15 | - | 53 | Tim Lees, Elliot Turner
2025-03-25 | Workshop - Next To Toilets bib tap | 13 | - | - | Tim Lees, Elliot Turner
2025-03-25 | Workshop - Next To Fire Exit Doors bib tap | 17 | - | - | Tim Lees, Elliot Turner
Unit 10- The Christy Estate
2025-03-25 | Entrances Male Toilets | 11 | - | 54 | Tim Lees, Elliot Turner | what 3 words: brief.eagle.sums
2025-03-25 | Entrances Female Toilets | 12 | - | 51 | Tim Lees, Elliot Turner
2025-03-25 | Kitchenette | 12 | - | 60 | Tim Lees, Elliot Turner
2025-03-25 | Workshop - Next to Tank | 14 | - | - | Tim Lees, Elliot Turner
2025-03-25 | Workshop - Next to Boiler | 15 | - | - | Tim Lees, Elliot Turner
2025-03-25 | Workshop - Fire Exit Doors | 16 | - | - | Tim Lees, Elliot Turner
2025-03-25 | Outside | 16 | - | - | Tim Lees, Elliot Turner
Unit 2- New Office (GU12 4UH)
2025-03-25 | Factory Floor- Bib Tap | 16 | - | - | Tim Lees, Elliot Turner | GU12 4UH
2025-03-25 | Ground Floor- Factory Kitchen | 13 | - | 69 | Tim Lees, Elliot Turner
2025-03-25 | Ground Floor- Male Toile off Factory Kitchen | 13 | - | 45 | Tim Lees, Elliot Turner | TMV (Hot)PRE : 62
2025-03-25 | Ground Floor- Factory Male Toilets | 10 | - | 60 | Tim Lees, Elliot Turner
2025-03-25 | Ground Floor- Factory Male Toilets cubicle | 10 | - | 36 | Tim Lees, Elliot Turner
2025-03-25 | Ground Floor Visitors Toilet | 13 | - | 41 | Tim Lees, Elliot Turner | TMV (Hot)PRE : 62
2025-03-25 | 1st Floor- Female Toilets | 14 | - | 62 | Tim Lees, Elliot Turner
2025-03-25 | 1st Floor- Male Toilets | 14 | - | 64 | Tim Lees, Elliot Turner
2025-03-25 | 1st Floor- Office Kitchen | 14 | - | 43 | Tim Lees, Elliot Turner
Unit 3
2025-04-10 | GF Visitors WC | 14 | - | 50 | Elliot Turner
2025-04-10 | Rumbler Bib Tap (hot) | - | - | 51 | Elliot Turner
2025-04-10 | 1st Floor- Finance Office | 13 | - | 51 | Elliot Turner
2025-04-10 | 1st Floor- Office Female Toilets | 12 | - | 53 | Elliot Turner
2025-04-10 | Factory/ Male Toilets | 13 | - | 45 | Elliot Turner
2025-04-10 | Workshop Kitchen Area | 12 | - | 55 | Elliot Turner
2025-04-10 | Directors Office Sink | 13 | - | 56 | Elliot Turner
2025-04-10 | 1st floor- Deburring Workshop | 12 | - | 55 | Elliot Turner
2025-04-10 | 1st floor- Cleaning Room- Bib Tap | 13 | - | - | Elliot Turner
2025-04-10 | Outside- Bib Tap | 16 | - | - | Elliot Turner
Unit 11
2025-04-10 | Mezzanine Kitchenette | 12 | - | 55 | Elliot Turner
2025-04-10 | Mezzanine Male Toilets | 13 | - | 53 | Elliot Turner
2025-04-10 | Mezzanine Female Toilets | 13 | - | 54 | Elliot Turner
2025-04-10 | Workshop- Next Roller Shutter Doors | 14 | - | - | Elliot Turner
2025-04-10 | Workshop- Near Fire Exit Door | 15 | - | - | Elliot Turner
Unit 14/15
2025-04-10 | Unit 15- Workshop Toilets WHB | 12 | - | 55 | Elliot Turner
2025-04-10 | Unit 14 - Workshop Toilets WHB | 12 | - | 61 | Elliot Turner
2025-04-10 | Unit 14- Workshop Sink | 13 | - | 59 | Elliot Turner
2025-04-10 | Unit 14- Mezzanine Sink | 12 | - | 54 | Elliot Turner
2025-04-10 | Unit 14 - Outside Bib Tap | 13 | - | - | Elliot Turner
Unit 16
2025-04-10 | Workshop Toilets - WHB | 12 | - | 42 | Elliot Turner | TMV (Hot) PRE - 56
2025-04-10 | Workshop Bib Tap (near toilet) | 15 | - | - | Elliot Turner
2025-04-10 | Mezzanine- Sink | 13 | - | 52 | Elliot Turner
Unit 19
2025-04-10 | Workshop Toilets | 13 | - | 41 | Elliot Turner | No access
2025-04-10 | Workshop Restroom/ Kitchen | 12 | - | 50 | Elliot Turner | No access
2025-04-10 | Workshop - Bib Tap | 16 | - | - | Elliot Turner | No access
Unit 1
2025-04-10 | Male Toilets | 13 | - | 41 | Elliot Turner | TMV (Hot)PRE : 54
2025-04-10 | Female Toilets | 12 | - | 40 | Elliot Turner
2025-04-10 | Kitchenette mezzanine floor | 15 | - | 51 | Elliot Turner
2025-04-10 | Workshop - Next To Toilets bib tap | 14 | - | - | Elliot Turner
2025-04-10 | Workshop - Next To Fire Exit Doors bib tap | 17 | - | - | Elliot Turner
Unit 10- The Christy Estate
2025-04-10 | Entrances Male Toilets | 13 | - | 48 | Elliot Turner | what 3 words: brief.eagle.sums
2025-04-10 | Entrances Female Toilets | 12 | - | 49 | Elliot Turner
2025-04-10 | Kitchenette | 14 | - | 58 | Elliot Turner
2025-04-10 | Workshop - Next to Tank | 15 | - | - | Elliot Turner
2025-04-10 | Workshop - Next to Boiler | 14 | - | - | Elliot Turner
2025-04-10 | Workshop - Fire Exit Doors | 12 | - | - | Elliot Turner
2025-04-10 | Outside | 13 | - | - | Elliot Turner
Unit 2- New Office (GU12 4UH)
2025-04-10 | Factory Floor- Bib Tap | 12 | - | - | Elliot Turner | GU12 4UH
2025-04-10 | Ground Floor- Factory Kitchen | 13 | - | 66 | Elliot Turner
2025-04-10 | Ground Floor- Male Toile off Factory Kitchen | 13 | - | 46 | Elliot Turner | TMV (Hot)PRE : 64
2025-04-10 | Ground Floor- Factory Male Toilets | 11 | - | 57 | Elliot Turner
2025-04-10 | Ground Floor- Factory Male Toilets cubicle | 12 | - | 39 | Elliot Turner | TMV (Hot)PRE : 64
2025-04-10 | Ground Floor Visitors Toilet | 15 | - | 42 | Elliot Turner | TMV (Hot)PRE : 64
2025-04-10 | 1st Floor- Female Toilets | 14 | - | 59 | Elliot Turner
2025-04-10 | 1st Floor- Male Toilets | 13 | - | 58 | Elliot Turner
2025-04-10 | 1st Floor- Office Kitchen | 13 | - | 40 | Elliot Turner
Unit 3
2025-05-27 | GF Visitors WC | 19 | - | 60 | Tim Lees
2025-05-27 | 1st Floor- Finance Office | 19 | - | 58 | Tim Lees
2025-05-27 | 1st Floor- Office Female Toilets | 19 | - | 58 | Tim Lees
2025-05-27 | Rumbler Bib Tap (hot) | - | - | 55 | Tim Lees
2025-05-27 | Factory/ Male Toilets WHB | 19 | - | 51 | Tim Lees
2025-05-27 | Workshop Kitchen Area | 19 | - | 60 | Tim Lees
2025-05-27 | Directors Office Sink | 19 | - | 51 | Tim Lees
2025-05-27 | 1st floor- Deburring Workshop | 19 | - | 51 | Tim Lees
2025-05-27 | 1st floor- Cleaning Room- Bib Tap | 19 | - | - | Tim Lees
2025-05-27 | Outside- Bib Tap | 19 | - | - | Tim Lees
Unit 11
2025-05-27 | Mezzanine Kitchenette | 19 | - | 56 | Tim Lees
2025-05-27 | Mezzanine Male Toilets | 19 | - | 56 | Tim Lees
2025-05-27 | Mezzanine Unisex Toilets | 19 | - | 51 | Tim Lees
2025-05-27 | Workshop- Next Roller Shutter Doors | 19 | - | - | Tim Lees
2025-05-27 | Workshop- Near Fire Exit Door | 19 | - | - | Tim Lees
Unit 14/15
2025-05-27 | Unit 15- Workshop Toilets WHB | 19 | - | 58 | Tim Lees
2025-05-27 | Unit 14 - Workshop Toilets WHB | 19 | - | 58 | Tim Lees
2025-05-27 | Unit 14- Workshop Sink | 19 | - | 60 | Tim Lees
2025-05-27 | Unit 14- Mezzanine Sink | 19 | - | 58 | Tim Lees
2025-05-27 | Unit 14 - Outside Bib Tap | 19 | - | - | Tim Lees
Unit 16
2025-05-27 | Workshop Unisex Toilets - WHB | 19 | - | 44 | Tim Lees | TMV (Hot) PRE - 63
2025-05-27 | Workshop Bib Tap (near toilet) | 19 | - | - | Tim Lees
2025-05-27 | Mezzanine- Sink | 19 | - | 59 | Tim Lees
Unit 19
2025-05-27 | Workshop Toilets | - | - | - | Tim Lees | No access
2025-05-27 | Workshop Restroom/ Kitchen | - | - | - | Tim Lees | No access
2025-05-27 | Workshop - Bib Tap | - | - | - | Tim Lees | No access
Unit 1
2025-05-27 | Male Toilets | 18 | - | 41 | Tim Lees | TMV (Hot)PRE : 54
2025-05-27 | Female Toilets | 18 | - | 54 | Tim Lees
2025-05-27 | Workshop - Next To Toilets bib tap | 19 | - | - | Tim Lees
2025-05-27 | Kitchenette mezzanine floor | 18 | - | 55 | Tim Lees
2025-05-27 | Workshop - Next To Fire Exit Doors bib tap | 20 | - | - | Tim Lees
Unit 10- The Christy Estate
2025-05-27 | Entrances Male Toilets | - | - | - | Tim Lees | No Access- Site Closed | what 3 words: brief.eagle.sums
2025-05-27 | Entrances Female Toilets | - | - | - | Tim Lees | No Access- Site Closed
2025-05-27 | Kitchenette | - | - | - | Tim Lees | No Access- Site Closed
2025-05-27 | Workshop - Next to Tank | - | - | - | Tim Lees | No Access- Site Closed
2025-05-27 | Workshop - Next to Boiler | - | - | - | Tim Lees | No Access- Site Closed
2025-05-27 | Workshop - Fire Exit Doors | - | - | - | Tim Lees | No Access- Site Closed
2025-05-27 | Outside | - | - | - | Tim Lees | No Access- Site Closed
Unit 2- New Office (GU12 4UH)
2025-05-27 | Factory Floor- Bib Tap | 16 | - | - | Tim Lees
2025-05-27 | Ground Floor- Factory Kitchen | 19 | - | 68 | Tim Lees
2025-05-27 | Ground Floor- Male Toile off Factory Kitchen | 19 | - | 41 | Tim Lees | TMV (Hot)PRE : 68
2025-05-27 | Ground Floor- Factory Male Toilets | 20 | - | 70 | Tim Lees
2025-05-27 | Ground Floor- Factory Male Toilets cubicle | 20 | - | 44 | Tim Lees | TMV (Hot)PRE : 66
2025-05-27 | Ground Floor Visitors Toilet | 20 | - | 42 | Tim Lees | TMV (Hot)PRE : 60
2025-05-27 | 1st Floor- Female Toilets | 19 | - | 58 | Tim Lees
2025-05-27 | 1st Floor- Male Toilets | 19 | - | 58 | Tim Lees
2025-05-27 | 1st Floor- Office Kitchen | 20 | - | 43 | Tim Lees
Unit 3
2025-06-19 | GF Visitors WC | 21 | - | 53 | Tim Lees
2025-06-19 | 1st Floor- Finance Office | 21 | - | 59 | Tim Lees
2025-06-19 | 1st Floor- Office Female Toilets | 21 | - | 58 | Tim Lees
2025-06-19 | Rumbler Bib Tap (hot) | - | - | 51 | Tim Lees
2025-06-19 | Factory/ Male Toilets WHB | 21 | - | 51 | Tim Lees
2025-06-19 | Workshop Kitchen Area | 22 | - | 55 | Tim Lees
2025-06-19 | Directors Office Sink | 22 | - | 53 | Tim Lees
2025-06-19 | 1st floor- Deburring Workshop | 22 | - | 51 | Tim Lees
2025-06-19 | 1st floor- Cleaning Room- Bib Tap | 22 | - | - | Tim Lees
2025-06-19 | Outside- Bib Tap | 22 | - | - | Tim Lees
Unit 11
2025-06-19 | Mezzanine Kitchenette | 21 | - | 56 | Tim Lees
2025-06-19 | Mezzanine Male Toilets | 21 | - | 63 | Tim Lees
2025-06-19 | Mezzanine Unisex Toilets | 21 | - | 63 | Tim Lees
2025-06-19 | Workshop- Next Roller Shutter Doors | 22 | - | - | Tim Lees
2025-06-19 | Workshop- Near Fire Exit Door | 22 | - | - | Tim Lees
Unit 14/15
2025-06-19 | Unit 15- Workshop Toilets WHB | 21 | - | 55 | Tim Lees
2025-06-19 | Unit 14 - Workshop Toilets WHB | 21 | - | 58 | Tim Lees
2025-06-19 | Unit 14- Workshop Sink | 21 | - | 58 | Tim Lees
2025-06-19 | Unit 14- Mezzanine Sink | 21 | - | 55 | Tim Lees
2025-06-19 | Unit 14 - Outside Bib Tap | 21 | - | - | Tim Lees
Unit 16
2025-06-19 | Workshop Unisex Toilets - WHB | 21 | - | 44 | Tim Lees | TMV (Hot) PRE - 65
2025-06-19 | Workshop Bib Tap (near toilet) | 21 | - | - | Tim Lees
2025-06-19 | Mezzanine- Sink | 21 | - | 53 | Tim Lees
Unit 19
2025-06-19 | Workshop Toilets | - | - | - | Tim Lees | No access
2025-06-19 | Workshop Restroom/ Kitchen | - | - | - | Tim Lees | No access
2025-06-19 | Workshop - Bib Tap | - | - | - | Tim Lees | No access
Unit 1
2025-06-19 | Male Toilets | 20 | - | 41 | Tim Lees | TMV (Hot)PRE : 54
2025-06-19 | Female Toilets | 20 | - | 54 | Tim Lees
2025-06-19 | Workshop - Next To Toilets bib tap | 20 | - | - | Tim Lees
2025-06-19 | Kitchenette mezzanine floor | 23 | - | 55 | Tim Lees
2025-06-19 | Workshop - Next To Fire Exit Doors bib tap | 23 | - | - | Tim Lees
Unit 10- The Christy Estate
2025-06-19 | Entrances Male Toilets | - | - | - | Tim Lees | No Access- Site Closed
2025-06-19 | Entrances Female Toilets | - | - | - | Tim Lees | No Access- Site Closed
2025-06-19 | Kitchenette | - | - | - | Tim Lees | No Access- Site Closed
2025-06-19 | Workshop - Next to Tank | - | - | - | Tim Lees | No Access- Site Closed
2025-06-19 | Workshop - Next to Boiler | - | - | - | Tim Lees | No Access- Site Closed
2025-06-19 | Workshop - Fire Exit Doors | - | - | - | Tim Lees | No Access- Site Closed
2025-06-19 | Outside | - | - | - | Tim Lees | No Access- Site Closed
Unit 2- New Office (GU12 4UH)
2025-06-19 | Factory Floor- Bib Tap | 25 | - | - | Tim Lees
2025-06-19 | Ground Floor- Factory Kitchen | 23 | - | 70 | Tim Lees
2025-06-19 | Ground Floor- Male Toile off Factory Kitchen | 23 | - | 39 | Tim Lees | TMV (Hot)PRE : 68
2025-06-19 | Ground Floor- Factory Male Toilets | 23 | - | 70 | Tim Lees
2025-06-19 | Ground Floor- Factory Male Toilets cubicle | 23 | - | 41 | Tim Lees | TMV (Hot)PRE : 63
2025-06-19 | Ground Floor Visitors Toilet | 23 | - | 41 | Tim Lees | TMV (Hot)PRE : 60
2025-06-19 | 1st Floor- Female Toilets | 23 | - | 54 | Tim Lees
2025-06-19 | 1st Floor- Male Toilets | 23 | - | 53 | Tim Lees
2025-06-19 | 1st Floor- Office Kitchen | 23 | - | 42 | Tim Lees
Unit 3
2025-07-28 | GF Visitors WC | 21 | - | 58 | Tim Lees
2025-07-28 | 1st Floor- Finance Office | 22 | - | 59 | Tim Lees
2025-07-28 | 1st Floor- Office Female Toilets | 22 | - | 58 | Tim Lees
2025-07-28 | Rumbler Bib Tap (hot) | - | - | 52 | Tim Lees
2025-07-28 | Factory/ Male Toilets WHB | 22 | - | 53 | Tim Lees
2025-07-28 | Workshop Kitchen Area | 22 | - | 55 | Tim Lees
2025-07-28 | Directors Office Sink | 22 | - | 58 | Tim Lees
2025-07-28 | 1st floor- Deburring Workshop | 22 | - | 52 | Tim Lees
2025-07-28 | 1st floor- Cleaning Room- Bib Tap | 22 | - | - | Tim Lees
2025-07-28 | Outside- Bib Tap | 22 | - | - | Tim Lees
Unit 11
2025-07-28 | Mezzanine Kitchenette | 21 | - | 54 | Tim Lees
2025-07-28 | Mezzanine Male Toilets | 21 | - | 60 | Tim Lees
2025-07-28 | Mezzanine Unisex Toilets | 21 | - | 60 | Tim Lees
2025-07-28 | Workshop- Next Roller Shutter Doors Bib Tap | 22 | - | - | Tim Lees
2025-07-28 | Workshop- Near Fire Exit Door Bib Tap | 23 | - | - | Tim Lees
Unit 14/15
2025-07-28 | Unit 15- Workshop Toilets WHB | 22 | - | 55 | Tim Lees
2025-07-28 | Unit 14 - Workshop Toilets WHB | 22 | - | 61 | Tim Lees
2025-07-28 | Unit 14- Workshop Sink | 22 | - | 61 | Tim Lees
2025-07-28 | Unit 14- Mezzanine Sink | 22 | - | 57 | Tim Lees
2025-07-28 | Unit 14 - Outside Bib Tap | 22 | - | - | Tim Lees
Unit 16
2025-07-28 | Workshop Unisex Toilets - WHB | 22 | - | 23 | Tim Lees | TMV (Hot)PRE : 23. No power to water heater, possible faulty fuse
2025-07-28 | Workshop Bib Tap (near toilet) | 22 | - | - | Tim Lees
2025-07-28 | Mezzanine- Sink | 22 | - | 53 | Tim Lees
Unit 1
2025-07-28 | Male Toilets | 21 | - | 52 | Tim Lees | TMV (Hot)PRE : 68
2025-07-28 | Female Toilets | 21 | - | 52 | Tim Lees
2025-07-28 | Workshop - Next To Toilets bib tap | 21 | - | - | Tim Lees
2025-07-28 | Kitchenette mezzanine floor | 22 | - | 51 | Tim Lees
2025-07-28 | Workshop - Next To Fire Exit Doors bib tap | 22 | - | - | Tim Lees
Unit 2- New Office (GU12 4UH)
2025-07-28 | Factory Floor- Bib Tap | 25 | - | - | Tim Lees
2025-07-28 | Ground Floor- Factory Kitchen | 23 | - | 68 | Tim Lees
2025-07-28 | Ground Floor- Male Toile off Factory Kitchen | 23 | - | 42 | Tim Lees | TMV (Hot)PRE : 68
2025-07-28 | Ground Floor- Factory Male Toilets | 23 | - | 70 | Tim Lees
2025-07-28 | Ground Floor- Factory Male Toilets cubicle | 23 | - | 41 | Tim Lees | TMV (Hot)PRE : 63
2025-07-28 | Ground Floor Visitors Toilet | 22 | - | 41 | Tim Lees | TMV (Hot)PRE : 60
2025-07-28 | 1st Floor- Female Toilets | 22 | - | 54 | Tim Lees
2025-07-28 | 1st Floor- Male Toilets | 22 | - | 53 | Tim Lees
2025-07-28 | 1st Floor- Office Kitchen | 22 | - | 42 | Tim Lees
Unit 3
| GF Visitors WC | 21 | - | 58 | Tim Lees
| 1st Floor- Finance Office | 22 | - | 59 | Tim Lees
| 1st Floor- Office Female Toilets | 22 | - | 58 | Tim Lees
| Rumbler Bib Tap (hot) | - | - | 52 | Tim Lees
| Factory/ Male Toilets WHB | 22 | - | 53 | Tim Lees
| Workshop Kitchen Area | 22 | - | 55 | Tim Lees
| Directors Office Sink | 22 | - | 58 | Tim Lees
| 1st floor- Deburring Workshop | 22 | - | 52 | Tim Lees
| 1st floor- Cleaning Room- Bib Tap | 22 | - | - | Tim Lees
| Outside- Bib Tap | 22 | - | - | Tim Lees
Unit 11
| Mezzanine Kitchenette | 21 | - | 54 | Tim Lees
| Mezzanine Male Toilets | 21 | - | 60 | Tim Lees
| Mezzanine Unisex Toilets | 21 | - | 60 | Tim Lees
| Workshop- Next Roller Shutter Doors Bib Tap | 22 | - | - | Tim Lees
| Workshop- Near Fire Exit Door Bib Tap | 23 | - | - | Tim Lees
Unit 14/15
2025-07-28 | Unit 15- Workshop Toilets WHB | 22 | - | 55 | Tim Lees
2025-07-28 | Unit 14 - Workshop Toilets WHB | 22 | - | 61 | Tim Lees
2025-07-28 | Unit 14- Workshop Sink | 22 | - | 61 | Tim Lees
2025-07-28 | Unit 14- Mezzanine Sink | 22 | - | 57 | Tim Lees
2025-07-28 | Unit 14 - Outside Bib Tap | 22 | - | - | Tim Lees
Unit 16
2025-07-28 | Workshop Unisex Toilets - WHB | 22 | - | 23 | Tim Lees | TMV (Hot)PRE : 23. No power to water heater, possible faulty fuse
2025-07-28 | Workshop Bib Tap (near toilet) | 22 | - | - | Tim Lees
2025-07-28 | Mezzanine- Sink | 22 | - | 53 | Tim Lees
Unit 1
2025-07-28 | Male Toilets | 21 | - | 52 | Tim Lees | TMV (Hot)PRE : 68
2025-07-28 | Female Toilets | 21 | - | 52 | Tim Lees
2025-07-28 | Workshop - Next To Toilets bib tap | 21 | - | - | Tim Lees
2025-07-28 | Kitchenette mezzanine floor | 22 | - | 51 | Tim Lees
2025-07-28 | Workshop - Next To Fire Exit Doors bib tap | 22 | - | - | Tim Lees
Unit 2- New Office (GU12 4UH)
2025-07-28 | Factory Floor- Bib Tap | 25 | - | - | Tim Lees
2025-07-28 | Ground Floor- Factory Kitchen | 23 | - | 68 | Tim Lees
2025-07-28 | Ground Floor- Male Toile off Factory Kitchen | 23 | - | 42 | Tim Lees | TMV (Hot)PRE : 68
2025-07-28 | Ground Floor- Factory Male Toilets | 23 | - | 70 | Tim Lees
2025-07-28 | Ground Floor- Factory Male Toilets cubicle | 23 | - | 41 | Tim Lees | TMV (Hot)PRE : 63
2025-07-28 | Ground Floor Visitors Toilet | 22 | - | 41 | Tim Lees | TMV (Hot)PRE : 60
2025-07-28 | 1st Floor- Female Toilets | 22 | - | 54 | Tim Lees
2025-07-28 | 1st Floor- Male Toilets | 22 | - | 53 | Tim Lees
2025-07-28 | 1st Floor- Office Kitchen | 22 | - | 42 | Tim Lees

## Annual TMVs
Annual Thermostatic Mixing Valve (TMV) Test & Service Records
Date | TMV / Location | TMV outlet °C / operating correctly? Y/N | Filters / strainers inspection / are they clean? Y/N | Name | Comments
2025-03-25 | Unit 16 - Workshop Toilets | Y | Y | Tim Lees | Passed fail safe test
2025-03-25 | Unit 1- Male/ Disabled Toilet | Y | Y | Tim Lees | Passed fail safe test

## Annual Expension Vessels
Annual Expansion Vessel Flushing & Inspection Records
Date | Expansion Vessel / Location | Flushed / Inspected / Repressurised? Y/N | Bladder Require Change? Y/N | Name | Comments
2025-05-27 | Unit 3- Deburring Workshop | NO | NO | Tim Lees | Unable to repressorise vessel due to location. Flushed system and inspected vessel- all ok
2025-05-27 | Unit 3- Workshop Kitchen Area | YES | NO | Tim Lees
2025-05-27 | Unit 3- Directors Office Sink | YES | NO | Tim Lees
2025-05-27 | Unit 11 Mezzanine Floor Kitchen | YES | YES | Tim Lees | Bladder compromised, vessel full of water. recommended to replace vessel
2025-05-27 | Unit 11- Mezzanine Male Toilets | YES | NO | Tim Lees
2025-05-27 | Unit 14- Workshop Sink | YES | NO | Tim Lees
2025-05-27 | Unit 15- Toilet | YES | NO | Tim Lees
2025-05-27 | Unit 16- Unisex Toilet | YES | NO | Tim Lees
2025-05-27 | Unit 16 Mezzanine Sink Kitchen | YES | NO | Tim Lees
2025-05-27 | Unit 19 Toilet | NO | N/A | Tim Lees | No Access to Unit, closed
2025-05-27 | Unit 1 Behind WC Panel | YES | NO | Tim Lees
2025-05-27 | Unit 1 Kitchenette | YES | YES | Tim Lees | Bladder compromised, vessel full of water. recommended to replace vessel
| Unit 10 Kitchen | NO | N/A | Tim Lees | No Access to Unit, closed